Note: The following information is to be used as guidelines only. The Host Network Project specific standards and approved drawings will take precedence over the general information provided in this document.

Trench Depths

| Installation Type | All Networks |
| --- | --- |
| Direct buried | >950mm |
| With cover slabs | >800mm |
| LV only | >750mm |

Trench Widths

| Electricity Cables Only |
| --- |
| Cable Type | SP AusNet, UED & Jemena | PCA/CP only |
| 1 LV | 300mm | 400mm |
| 2 LV | 400mm | 400mm |
| 1 HV | 400mm | 400mm |
| 2 HV | 600mm | 400mm |
| 1 HV 1 LV | 600mm | 400mm |
| 1 HV 2 LV | 600mm | 500mm |
| 1 HV 3 LV | 750mm | 600mm |
| 2 HV 1 LV | 750mm | 500mm |
| 2 HV 2 LV | 750mm | 600mm |
| 2 HV 3 LV | 900mm | 700mm |

| Shared Trench with 1 x P50 Telecom |
| --- |
| Cable Type | SP AusNet, UED & Jemena | PCA/CP only |
| 1 LV | 450mm | 600mm |
| 2 LV | 600mm | 600mm |
| 1 HV | 600mm | 600mm |
| 2 HV | 750mm | 900mm |
| 1 HV 1 LV | 750mm | 900mm |
| 1 HV 2 LV | 750mm | 900mm |
| 1 HV 3 LV | 900mm | 1100mm |
| 2 HV 1 LV | 900mm | 1100mm |
| 2 HV 2 LV | 900mm | 1100mm |
| 2 HV 3 LV | 1100mm | 1100mm |

| Shared Trench with 1 x P50 Telecom & 1x 100mm Telco |
| --- |
| Cable Type | SP AusNet, UED & Jemena | PCA/CP only |
| 1 LV | 600mm | 600mm |
| 2 LV | 600mm | 750mm |
| 1 HV | 750mm | 750mm |
| 2 HV | 900mm | 900mm |
| 1 HV 1 LV | 750mm | 900mm |
| 1 HV 2 LV | 900mm | 900mm |
| 1 HV 3 LV | 1100mm | 1100mm |
| 2 HV 1 LV | 1100mm | 1100mm |
| 2 HV 2 LV | 1100mm | 1100mm |
| 2 HV 3 LV | Not permitted | 1200mm |

Cable Depths

All measurements are from the top of cables to final ground level.

Table 1: Direct Buried with No Mechanical Protection

| Voltage | Cable type | Measurement of cover to top of cable |
| --- | --- | --- |
| <1kv | Single Core | N/A |
|  | Multi Core | >750mm |
| <22kv | All | >750mm |
| <66kv | All | >1000mm |

Table 2: Direct Buried - Open Trench and Slabbed Protection

| Voltage | Cable type | Measurement of cover to top of cable |
| --- | --- | --- |
| <1kv | Single Core | >600mm |
|  | Multi Core | >600mm |
| <22kv | All | >600mm |
| <66kv | All | >750mm |

Table 3: Direct Buried or Bored in Approved Conduits

| Voltage | Cable type | Measurement of cover to top of conduit |
| --- | --- | --- |
| <1kv | Single Core | >600mm |
|  | Multi Core | >600mm |
| <22kv | All | >600mm |
| <66kv | All | >750mm |

Installation of Backfill

| Bottom of trench to cable | Top of cable to cover slab |
| --- | --- |
| >100mm | >100mm |

- Unless otherwise approved by the network owner all backfill material below the cover slabs and must be sand. Sand used must comply with standard, see GA211 pg 4 Powercor Document – Washed Concrete Sand ( AS2758.1)

- There must be more than 50mm of backfill material under the cables and between cable and cover slabs after compaction

- The cables must be clear of any rocks or hard/sharp objects.

Installation of Protection and Marking Tape

- Cover slabs to be positioned 100mm +- 50mm from the top of cables after compaction.

- Cover slabs must protect (be located over) all cables.

- Marker tape must be located 300mm below ground level and directly over cables and conduits +- 50mm except in cases where the conduits were installed using boring techniques.

Service Pits

- Level with the final ground level.

- If in concrete – >150 mm of concrete encasement required from rim of pit

- No expansion joints within 150mm of the pit rim

- Conduit to protrude into pit 75mm +- 25mm

- Pits to be free of rumble

- Correctly fitted lid.

Separation between Cables and Other Assets

For separation details refer to the Network Owners Standards and the projects specifications.